MASTER SPECIFICATION FOR SH and H MODELS

## JOB NAME:_______________________________ 	 ENGINEER:___________________________________

REPRESENTATIVE:_______________________	CONTRACTOR:_______________________________

# GENERAL

Provide a quantity of _______ packaged type electric water heater(s) Model No. _____________________ as manufactured by HUBBELL The Electric Heater Co., Stratford, CT.  The pressure vessel section, including the electrical control panel, shall be mounted on structural supports and be suitably insulated, jacketed, painted, and provided with lifting lugs.  The entire unit is to be packaged ready for plumbing and electrical service connections and shall bear the UL listing mark certifying the entire water heater.

# PRESSURE VESSEL

The pressure vessel shall be all welded construction and ASME Code Section IV stamped for a working pressure of 125 psi (Optional Specification: Select 100, 150, 160, ____psi) and contain a minimum of _______ gallons of storage.  The storage vessel shall be carbon steel and lined with seamless Hydrastone Cement to a minimum thickness of 5/8" on 100% of all interior tank surfaces (Optional Specifications: Phenolic lined steel tank, 3lb/Sq Ft Copper lined steel tank, Hot dipped galvanized steel tank, Flame spray copper coated steel tank, Solid copper-silicon tank, solid 90/10 copper-nickel tank, solid Type 304 or 316L stainless steel tank).  The pressure vessel is to be completely covered with 2" thick "E" type energy conservation fiberglass blanket insulation and enclosed in a heavy gauge galvanized steel metal jacket finished in gray hammertone enamel.  An ASME approved automatic reseating combination temperature and pressure relief valve set at the tank WP and 210°F shall protect the vessel.

RECOVERY

The recovery section shall be rated at _______ kW which will heat _________GPH of water at ________°F rise (________° to ________°F).

# ELECTRICAL

The heater shall be designed to operate at _____ volts, _____ phase, ____Hz, with a fused low voltage transformer providing 120 volt to all operating controls.  The immersion heating element(s) shall be high quality copper sheathed (Optional Specifications: Incoloy, Type 304 or 316 stainless steel) and sized to obtain the rated recovery.  Each element circuit is to be independently operated through a definite purpose magnetic contactor having a resistive load rating equal to or exceeding the ampere rating of that particular circuit and shall be protected by individual power fuses rated at approximately 125% of the ampacity of the circuit.  Multiple circuit elements shall be provided with a master 	terminal block for connecting of the incoming power feeds (Optional Specification: a built-in non-fused On/Off disconnect switch, Built-in circuit breaker with On/Off handle).  A safety door interlock switch shall interrupt power to the control circuit when the control panel door is 	opened. The control thermostat shall be immersion type and shall be consistent with the recovery rate of the heating element as to the number of steps required.  A hi-limit control with a manual reset button shall be factory installed to disconnect all ungrounded conductors to the heating element(s) in the event of an over-temperature condition in the storage section.

In addition, the water heater shall be supplied with the following optional features:

OPTION 	_________________________________________________

OPTION 	_________________________________________________

OPTION 	_________________________________________________

WARRANTY

The water heater manufacturer shall warranty all electrical components against defects in workmanship and material for a period of one (1) year 	from date of start-up, and the pressure vessel for a full five (5) years Non Pro-Rated (Optional Specification: full ten (10) years Non Pro-Rated) 	from date of start-up, provided that the unit is started within three (3) months of date of shipment and installed and operated within the scope of 	the tank design and operating capability.  Each water heater shall be shipped with a complete set of installation and operating instructions including spare parts list and approved drawing.